## Slide 1: Cogeneration and trigeneration:
prof. Mauro REINI
docente di sistemi per l’energia e l’ambiente
Università di Trieste – Polo di Pordenone

## Slide 2: Cogeneration and trigeneration:
Summer production of chilled water and
integration with heat & cold district networks
prof. Mauro REINI
docente di sistemi per l’energia e l’ambiente
Università di Trieste – Polo di Pordenone

## Slide 3: The choice of a cogeneration plant
It involves numerous decision-making aspects:
- A pre-feasibility analysis, to establish the technical-economic conditions that allow to obtain the desired advantages,
- Feasibility and project analysis, to define:
- Type of system;
- Size of the system;
- Management and control criteria;
- Tariff and regulatory aspects.
To do this it may be necessary:
- Develop a technical-economic model of the system;
- Pair it with simulation / optimization techniques.

## Slide 4: The choice of a cogeneration plant
Starting point:
Knowledge of energy data,
Knowledge of economic data.
The choice of the cogeneration system can be supported by simulation / optimization at different levels:
Comparison between different sizes or technological solutions,
Definition of the thermal part and its components,
Choice of management strategy, in a given context,
Integration with other cogeneration plants,
Integration with heat or cold transmission networks.

## Slide 5: Trend of the thermal demand
Need for extensive usege of cogenerated heat
1st management hypothesis: tracking the thermal demand
[kW] richiesti

## Slide 6: Duration curve of the thermal demand
The preliminary sizing can be done based on the duration curve of the thermal demand.
[kW] richiesti
Maximum power of the cogenerator
Minimum thermal ower in modulation
Full load
Partial load
Cogenerator off
Thermal peak

## Slide 7: Duration curve of the thermal demand
In general , the maximum power of the cogeneratior is decidely lowen then the maximum demand
[kW] richiesti
Max thermal power of the cogenerator
Min thermal power in the modulation
Full load
Potental load
Cogenerator off
Thermal peak with the integration boiler

## Slide 8: Power segmentation
It allows to cover the therml load more extensively
It implies higher installation cost of CHP system
[kW] richiesti
Max thermal power of the 2 cogenerators
Min thermal power x 1 in modulation
Full load x2
Partial load x2 x1
Cogeneretor off
thermal peak with the integration boile

## Slide 9: Tri-generative systems
All seasonal utilities are affected by reduced use of the cogenerator in summer: Extensive use of integration heat, reduction of the annual CHP efficiency, long PBPs

## Slide 10: Tri-generative systems
The tri-generative systems allow the use of cogenerated heat even in summer, producing chilled water.

## Slide 11: Absorption cooling machines
Thermal Compression
Conventional refrigeration cycle
1
5
6
8
2
3
4
10
9
7

## Slide 12: Absorption cooling machines
For water and ammonia,
the generator is 130 ° -150° C and 45 ° -55 °C in the absorber /condenser. The temperature at the evaporator (function of pv) is a few degrees below zero.
Other mixtures are also used, like water-lithium bromide or water-lithium fluoride mixtures (it is the water that acts as a refrigerant), which have the advantage of working at a lower temperature (around 80 ° C).

## Slide 13: Absorption cooling machines

## Slide 14: Absorbation cooling machine

## Slide 15: Abaco di Bosnjacovic

## Slide 16: Abaco di Bosnjacovic

## Slide 17: Double Effect Absorption Chillers

## Slide 18: Double Effect Absorption Chillers

## Slide 19: Absorption / Adsorption Chiller

## Slide 20: Solar cooling

## Slide 21: Solar cooling

## Slide 22: Solar cooling

## Slide 23: Tri-generative systems with MTG

## Slide 24: Possible uses of trigeneration
Hospistal
Public officies
Residence

## Slide 25: Variability of utility loads during the typical day

## Slide 26: ABSORPTION POWER CYCLE

## Slide 27: ABSORPTION POWER CYCLE

## Slide 28: ABSORPTION POWER CYCLE

## Slide 29: ABSORPTION POWER CYCLE
Dühring diagram for a LiBr aqueous solution, highlighting a typical absorption refrigeration cycle and the power cycle presented in Novotny and Kolovratnik - Int. J. Energy Res. 2017; 41:952–975, both with a highest solution temperature of 90°C.

## Slide 30: ABSORPTION POWER CYCLE
Results of thermodynamic analysis for 100 °C heat source. Novotny, Vitvarova, and Kolovratnik - Absorption Power Cycles with Various Working Fluids for Exergy-Efficient Low-Temperature Waste Heat Recovery.
u = energy utilization; gross = without considering auxiliary power for heat dissipation; c = cycle only; ex = exergy

## Slide 31: Synthesis of distributed cogeneration and district heating systems
Hypothesis of cogeneration distributed with MTG, integrated with micro-district heating networks, for the historic center of Pordenone.
The developed model includes:
- a set of micro-cogeneration gas turbines, located inside 6 buildings,
- a centralized cogeneration system, (600 kWe) allowing the required thermal energy to be produced in a single site

## Slide 32: Synthesis of distributed cogeneration and district heating systems
Distributed cogeneration
scheme system

## Slide 33: Synthesis of distributed cogeneration and district heating systems
ALTERNATIVES:
If you choose the centralized cogeneration system, generally based on an internal combustion engine (ICE):
cogenerated heat must be distributed to users and a district heating system must be built within a high density area of ​​historic buildings.
The investment cost of the entire system increases,
If you choose the cogeneration system distributed with mTG:
These have a higher cost per installed kWe,
They also have a lower electrical efficiency than ICE.

## Slide 34: Synthesis of distributed cogeneration and district heating systems
Choose whether the centralized engine should be adopted or not,
Define the number of micro-turbines (of fixed size) within each building,
Define the "minimum" correct connections between buildings, in order to optimize energy consumption at low thermal load,
Define the optimal strategy of system operation,
Assess the overall reduction of emissions, particularly CO2.
Goals :

## Slide 35: Synthesis of distributed cogeneration and district heating systems
The problems:
choosing whether the ICE has tobe adopted or not,
defining the number of micro turbines (of fixed size) inside each building,
defining“minimum” proper connections among buildings, in order to optimize energy consumption at low thermal load,
defining the operation strategy of the whole system,
to evaluate global CO2 emissions reduction

## Slide 36: Synthesis of distributed cogeneration and district heating systems
define a Full Mixed Linear Programming program (MILP),
solve it by means of a commercial software,
OBJ: Total annual cost for acquiring, maintaining and managing the entire system,
Taking into account the economic constraints: interest rate, price of gas and electricity, cost of components and plant integration,….
taking into account the physical constraints: thermal and electrical demands of the users over time, effect of the ambient temperature on the efficiency of the turbines,….
Solutions:

## Slide 37: Synthesis of distributed cogeneration and district heating systems
Methodology 1
defining a Mixed Integer Linear Program (MILP),
solving it by means of a commercial software,
OBJ: Total Annual Cost for owning, maintaining and operating the whole system,
taking the time dependent cost rate of gas and electricity into account to evaluate incomes and integrations from the outside,
taking account of ambient temperature effect on turbine efficiency.

## Slide 38: Synthesis of distributed cogeneration and district heating systems
The whole year is modeled with 3 "typical days", for energy demand, and 24 "typical days" for the value of the electricity sold to the grid.
Energy demand:
Electric demand
Thermic demand

## Slide 39
MILP models
OBJ is linear towards the variables that express the consumption of CHP systems;
Binary variables are used to express the presence / absence of mTG, ICE and network sections,
In addition to the on / off status of the machines.
In each time interval the optimization must take into account the constraints:
The performance curves of the components (variable with temperature) must be respected;
The thermal demand must be satisfied by cogenerators and auxiliary boilers;
The electricity demand must be satisfied by the cogenerators and by the integration with the network;
The thermal nodes must be balanced and all the branches have a loss proportional to their length.

## Slide 40: Synthesis of distributed cogeneration and district heating systems
Optimal configurations depending on the surrounding economic conditions: a + c) estimated life of the machines and network estimated at 13/26 years; b) 4.5 / 9 years; c) of 8/16 years; Savings vary between 1 - 8%.

## Slide 41: Synthesis of distributed cogeneration and district heating systems
Example of optimal management for the mTG only present in configuration b:
Thermal tracking is NOT the optimal solution (even the electrical one).

## Slide 42: Integration of CHP with absorption machines and district-cooling networks
Fuel (gas naturale)
Hot water (tele-heating)
Cold water (tele-cooling)

## Slide 43
Years of capital amortization:
10 for the machines, 20 for the network
Ut. isolate
UT in network
Integration of CHP with absorption machines and district-cooling networks

## Slide 44
TRIGENERATION APPLIED TO ISOLATED UTILITIES AND TO NETWORKED UTILITIES
 | Ut insolate | Ut. In Network
n° mTG | 11 | 10
n° mAS | 11 | 10
Investment [€] | 1.368.750 | 1.482.505
Operatic cost [€/anno] | 685.332 | 632.858
Annual cost [€/anno] | 862.591 | 812.041
Saving index | 26,87% | 31,15%
IRE | 9,73% | 12,70%
TEP saves | 93 | 132
Pay Back Period [months] | 33 | 32
Ut. insolate
Ut. in network
Integration of CHP with absorption machines and district-cooling networks

## Slide 45
Chart: 
| IRE
Utenze in rete-Trigenerazione(DI-CCHP) | 0.127
Utenze isolate-Trigenerazione(IS-CCHP) | 0.0973
Utenze in rete-Cogenerazione(DI-CHP) | 0.1534
Utenze isolate-Cogenerazione(IS-CHP) | 0.1411
Chart: [k€]
| Costo di investimento | Funzione obiettivo
Utenze in rete-Trigenerazione(DI-CCHP) | 1482.505 | 812.041
Utenze isolate-Trigenerazione(IS-CCHP) | 1368.75 | 862.591
Utenze in rete-Cogenerazione(DI-CHP) | 1040.451 | 1140.497
Utenze isolate-Cogenerazione(IS-CHP) | 660 | 1142.396
Chart: 
| I.R.
 | 0.3115
 | 0.2687
 | 0.0331
 | 0.0314
Cogeneration VS trigeneration
Economic parameters
Chart: [TEP]
| TEP risparmiate
 | 132
 | 93
 | 111
 | 73
Environmental parameters
Chart: [Mesi]
| Pay-back
 | 32
 | 33
 | 77
 | 64
Integration of CHP with absorption machines and district-cooling network

## Slide 46
Evolution DHN systems
The integrated energy system makes it possible to use all locally available energy sources to generate heat;
a large variety of fuels can be used: natural gas, biomass, municipal solid waste, coal, fuel oil.
Heat can also be produced by industrial plants, or by natural sources (eg, geothermal phenomena) and then conveyed into the distribution network.

## Slide 47: Context
CURRENT:
Large plants fueled with "valuable" fuels with yields of 40 - 50%,
Very small ONLY thermal systems, also powered by "valuable" fuels.
FUTURE (distributed generation):
Large plants fueled with different fuels ("valuable" and not) with yields of 40 - 60%,
Many medium and small COGENERATIVE systems fed with renewable or methane sources, adapted to the local thermal demand.

## Slide 48: Context
Current network:
With shaft, with few productive knots.
Many simple users, civil and industrial.
Significant transmission losses.
Future network:
Knitted, with many productive knots.
Some nodes with energy storage capacity.
Great importance to the management activity to guarantee the "quality" of the energy supplied.
Reduced transmission losses

## Slide 49: Conclusions
Cogeneration is a rational answer to the demand for energy efficiency;
It is possible to obtain important energy-environmental benefits also using gas-powered cogeneration systems;
The environmental benefits are even more evident by realizing cogeneration systems powered by RES (biomass, solar, ..);
An essential condition for actually obtaining the expected benefits is that as much as possible of the cogenerated heat is used usefully;
Small plants and tri-generative systems are advantageous if they result from an optimized symptesis and management

## Slide 50: Cogeneration and trigeneration
prof. Mauro REINI
docente di sistemi per l’energia e l’ambiente
Università di Trieste – Polo di Pordenone
Thanks for the attention