## Summer
t_ext | 35 | °C | extern
phi_ext | 70 | % | extern RH
t_int | 27 | °C | internal t
phi_int | 50 | % | internal RH
V | 2861 | m^3
people | 250
vent | 0.008 | m^3/s/person
sens | 70 | W/person
lat | 50 | W/person
Q_sens | 19781 | W
Q_sperson | 17500 | W
Q_lat | 12500 | W
Q_sens_tot | 37281 | W
Q_tot | 49781 | W
r_0 | 2500 | kJ/kg | calore latente
r1 | 9.9562 | kJ/g_V
r2 | 0.7489
n_max | 5-6 | air change rate
G_rinn | 7200 | m^3/h
G_max | 14305 | m^3/h
G_tot | 14305 | m^3/h
G_ric | 7105 | m^3/h
x_a | 0.01125 | kgv/kga
x_E | 0.02525 | kgv/kga
h_A | 56 | kJ/kg
h_E | 100 | kJ/kg
x_M | 0.018296 | gv/kga
theta_w_in | 7 | °C
theta_w_out | 12 | °C
theta_coil_m | 9.5 | °C
Dx | 10 | g_v/kg_a
theta_s | 12.5 | °C
G_ren/G_tot |  | %
cp_a | 1.005 | kJ/(kg K)
cp_v | 1.875 | kJ/(kg K)
cp_au | 1.0261 | kJ/(kg K)
c_l | 4.187 | kJ/(kg K)
Delta theta | 7.6196 | K
theta_I | 19.3804 | °C
theta_I | 19 | °C
Delta theta | 8 | K
G | 13624.8515 | m^3/h
G'_ric | 6424.8515 | m^3/h
x_M | 0.018648 | g_v/kg_a
h_p | 39 | kJ/kg
h_S | 35.5 | kJ/kg | x_p | g_v/kg_a
h_M | 79.5 | kJ/kg
x_i | 0.00975 | gv/kga
FB | 0.079545
m_l | 0.040412 | kg/s
phi_r | 199.8312 | kW | without water from condensation
phi_r |  | kW
phi_l | 101.0311 | kW
h_i | 44 | kJ/kg
phi_post | 22.7081 | kW
portata acqua refrigerazione
cl | 4.079 | kJ/(kg K) | specific heat of water with glicole
m_wc | 2.4408 | kg/s
mass flow rate of postheating coil
cl | 4.187 | kJ/(kg K)
theta_w_in | 60 | °C
theta_w_out | 50 | °C
m_wh | 0.54235 | kg/s | mass water heating coil